DRINKING WATER PRODUCTION TECHNOLOGY

---
TECHNICAL CONTENT
TECHNICAL CONTENT
PROJECT SPECIFICATION
Purpose of treatment:	Water production in drinking water quality from river water
Treated water quantitative demand:	10,0 m3/h
Treated water quality:	Drinking water quality
Technological water data:	you can find it in the technological data
Treatment method:	Ultrafiltration and reverse osmosis membrane technology
Location:	in 40’ container
Additional units:	Electric power supply, Bottling machine which is	not quoted in this offer.
System operation:	automatic

---
TREATMENT TECHNOLOGY
TREATMENT TECHNOLOGY
  - PRE-TREATMENT PROCESS
- Raw water pump
- Chlorinating dosing
- Pre-filter
- Ultrafiltraion
- Filtrate storage tank
  - DESALINATION PROCESS
- Dechlorinating dosing
- Antiscalant dosing
- Reverese Osmosis desalination
- Desinfection with chlorine
  - DRINKING WATER STORAGE AND FORWARDING
- UV treatment
 - Drinking water supply

---
Ultra-filtration
Ultra-filtration
Ultra-filtration (in short UF) is the most effective solution to remove the suspended solids, organic and inorganic colloids from raw water. The UF membrane is permeable by the dissolves salts and water molecules, but it retains the bigger contaminants like colloids or other filterable materials. The turbulent flow on the membrane surface continuously removes the retained contaminants from the membrane surface, preventing their deposition. The fluid passes on the membranes and the retained solution drained as retentate.

---
Reverse osmosis
Reverse osmosis
The reverse osmosis technology (in short RO) is a membrane separation process in which the applied membrane is permeable by the solution – water molecules – but it retains the main parts of the dissolved salts. The salts retained by the membrane during the process are delivered as concentrate, and the solution permeated on the membrane elements are delivered as permeate. We apply spiral wounded membrane elements with high permeate flux, as well as booster pump for negotiation of osmotic pressure.

---
TECHNOLOGICAL DATA
TECHNOLOGICAL DATA
Parameters		Raw water		Ultrafiltration pretreatment		Reverse osmosis desalination		Drinking water / (UF filtrate + RO permeate)
		River water	After the existing pre-treatment	UF feed water	UF filtrate	RO feed water	RO permeate
Flow rate:	m3/h			14,5	12,5 + 0,5	12,5	9,5	10 (0,5+9,5)
Quality
- Turbidity	NTU	12,5	2,4		< 0,4		non detectable	non detectable
- SDI					< 3	< 3	-	-
- pH value		7,48	7,27		7,27		5,8 – 6,5	6,5 – 7,5
- Electric conductivity	µS/m	11207	11016		11016		155	1280
- Total alkalinity	CaCO3	180	164		73		3,78	12,7
- Total hardness	CaCO3	1352	1272		1272		3,14	70,8
- Calcium	mg/l	272	256		256		0,6	14,2
- Magnesium	mg/l	164	154		154		0,4	8,6
- Chloride	mg/l	3510	3460		3460		61	232,8
- Sulphate	mg/l	1122	1062		1062		1,8	57,8
- Sodium	mg/l	2274	2241		2241		38,6	150,4
- Potassium	mg/l	38,3	35,7		35,7		0,8	2,6
- Total iron content	mg/l	Nil	Nil		-		-	-
- Aluminium	mg/l	/	0,051		0,051		0,01	0,01
- Total dissolved solids	mg/l	7524	7388		7388		108,9	860
- Total suspended solids	mg/l	98	26		< 0,5		non detectable	non detectable
- Free chlorine	mg/l	/	3		< 0,1	< 0,05	-	0

---
TECHNICAL AND PRICE SPECIFICATION OF THE SYSTEM
Nr.	Description	Design mark	Type	Qty	Capacity	Dimensions [m]	Weight [kg]	Installed electric energy [kW]
1.	ULTRA-FILTRATION UNIT
	- UF equipment	UF-1	HF-UF-15.0	1	Q=14,5 m3/h	3,0 x 1,5 x 2,2	1600	8,5
	- Pre-filter	FF-1	HF-FF-15.0 / 300	1	Q=14,5 m3/h
	- Chemical dosing stations	DP-1,2,3,4	HF-VA-ST/C-6-10	1				0,1
	- Storage tank	TT-1	HF-TT-2.0	1	V=2 ,0 m3	1,0 x 1,0 x 2,0	2200
2.	REVERSE OSMOSIS DESALINATION UNIT
	- everse osmosis desalination equip.	RO-1	HF-RO-10.0	1	Q= 9,5 m3/h	3,5 x 1,2 x 2,0	1400	21,5
	- Chemical dosing stations	DP-5-6-7	HF-VA-ST/C-6-10	1				0,1
3.	TREATED WATER STORAGE AND FORWARDING EQUIPMENT
	- Storage tank	TT-2	HF-TT-5.0	1	V=5,0 m3	2,2 x 1,2 x 2,2	5400
	- UV equipment	UV	Aquada-10	1	Q=10 m3/h			0,5
	- Forwarding pump with frequency converter	P05, P06		2	Q=2,5-6,5 m3/h	0,8 x 0,6 x 1,2		2 x 1,5
	- 10,0 m3/h forwarding pump	P07		1	Q= 10 m3/h H=40	0,5 x 0,6 x 1,2		2,2
4.	CONTAINER CONSTRUCTION
	- Container	40’		1				3,0
	- Building services and electricity			1
6.	ELECTRICITY AND COMPRESSED AIR SUPPLY
	- Aggregator			1
	- Compressor			1				1,1